## Schedule 1A
EnMasse
SCHEDULE No. 1A: Plant and Mandatory Spares Supplied from Abroad
.+150/-50 MVAR Static VAR Compensator (SVC) at 132kV Gawadar Old Grid Station
Item | Description | Qty. | Country of Origin | Unit Price | Total Price | Taxes and Duties
|  |  |  | CIP (PKR) | (PKR) | PKR
1 | 2 | 3 | 4 | 5 | 6=3x5 | 7
1 | Design, Manufacture, Supply, installation, testing & commissioning of +150/-50MVAR Static Var Compansator (SVC), capable of high-speed response to control system transient voltage stability, plant having major equipment like Transformer, Thyristor Controlled Reactor (TCR) , Thyristor Switched Capacitors (TSC), Harmonic Filters, circuit breakers, instrument transformers, disconnectors, fast acting controllers, cooling system, plant protection etc. | Lot
The design of SVC shall meet the operational and system dynamic requirements, specified in specification and harmonic/power quality survey results attached herewith, using any configuration of Thyristor Controlled Reactors (TCR), Thyristor Switched Capacitors (TSC), fixed capacitors and harmonic filter circuits. The full dynamic range shall consist of thyristor controlled reactors and/or thyristor switched capacitors except fixed capacitors. Temporary overload of specific components shall also be considered. The harmonic filter requirements have to be fulfilled over the whole reactive power range for harmonic emission from the grid as well as SVC system.
2 | Training as per Annexure-E | Lot
3 | O&M supervision as per Annexure-F | Lot
Total Column 7 to be carried forward to Grand Summary.
Name Of Bidder :
Signature of Bidder :

## Schedule 1B
EnMasse
SCHEDULE No. 1B: Plant and Mandatory spares Supplied from Abroad
.+150/-50 MVAR Static VAR Compensator (SVC) at 132kV Panjgoor Grid Station
Item | Description | Qty. | Country of Origin | Unit Price | Total Price | Taxes and Duties
|  |  |  | CIP (PKR) | (PKR) | PKR
1 | 2 | 3 | 4 | 5 | 6=3x5 | 7
1 | Design, Manufacture, Supply, installation, testing & commissioning of +150/-50MVAR Static Var Compansator (SVC), capable of high-speed response to control system transient voltage stability, plant having major equipment like Transformer, Thyristor Controlled Reactor (TCR) , Thyristor Switched Capacitors (TSC), Harmonic Filters, circuit breakers, instrument transformers, disconnectors, fast acting controllers, cooling system, plant protection etc. | Lot
The design of SVC shall meet the operational and system dynamic requirements, specified in specification and harmonic/power quality survey results attached herewith, using any configuration of Thyristor Controlled Reactors (TCR), Thyristor Switched Capacitors (TSC), fixed capacitors and harmonic filter circuits. The full dynamic range shall consist of thyristor controlled reactors and/or thyristor switched capacitors except fixed capacitors. Temporary overload of specific components shall also be considered. The harmonic filter requirements have to be fulfilled over the whole reactive power range for harmonic emission from the grid as well as SVC system.
2 | Training as per Annexure-E | Lot
3 | O&M supervision as per Annexure-F | Lot
Total Column 7 to be carried forward to Grand Summary.
Name Of Bidder :
Signature of Bidder :

## Schedule 2A
EnMasse
SCHEDULE No. 2A: Plant and Mandatory Spare supplied from within the Employer's Country
.+150/-50 MVAR Static VAR Compensator (SVC) at 132kV Gawadar Old Grid Station
Item | Description | Qty. | EXW Unit Price | Total EXW Price | Sales Tax | Total Price
1 | 2 | 3 | 4 | 5=3x4 | 6 | 7
1 | Design, Manufacture, Supply, installation, testing & commissioning of +150/-50 MVAR Static Var Compansator (SVC), capable of high-speed response to control system transient voltage stability, plant having major equipment like Transformer, Thyristor Controlled Reactor (TCR) , Thyristor Switched Capacitors (TSC), Harmonic Filters, circuit breakers, instrument transformers, disconnectors, fast acting controllers, cooling system, plant protection etc. | Lot
The design of SVC shall meet the operational and system dynamic requirements, specified in specification and harmonic/power quality survey results attached herewith, using any configuration of Thyristor Controlled Reactors (TCR), Thyristor Switched Capacitors (TSC), fixed capacitors and harmonic filter circuits. The full dynamic range shall consist of thyristor controlled reactors and/or thyristor switched capacitors except fixed capacitors. Temporary overload of specific components shall also be considered. The harmonic filter requirements have to be fulfilled over the whole reactive power range for harmonic emission from the grid as well as SVC system.
| Training as per Annexure-E | Lot
| O&M supervision as per Annexure-F | Lot
Total Column 5 to be carried forward to Grand Summary.
Name Of Bidder :
Signature of Bidder :

## Schedule 2B
EnMasse
SCHEDULE No. 2B: Plant and Mandatory Spare supplied from within the Employer's Country
.+150/-50 MVAR Static VAR Compensator (SVC) at 132kV Panjgoor Grid Station
Item | Description | Qty. | EXW Unit Price | Total EXW Price | Sales Tax | Total Price
1 | 2 | 3 | 4 | 5=3x4 | 6 | 7
1 | Design, Manufacture, Supply, installation, testing & commissioning of +150/-50MVAR Static Var Compansator (SVC), capable of high-speed response to control system transient voltage stability, plant having major equipment like Transformer, Thyristor Controlled Reactor (TCR) , Thyristor Switched Capacitors (TSC), Harmonic Filters, circuit breakers, instrument transformers, disconnectors, fast acting controllers, cooling system, plant protection etc. | Lot
The design of SVC shall meet the operational and system dynamic requirements, specified in specification and harmonic/power quality survey results attached herewith, using any configuration of Thyristor Controlled Reactors (TCR), Thyristor Switched Capacitors (TSC), fixed capacitors and harmonic filter circuits. The full dynamic range shall consist of thyristor controlled reactors and/or thyristor switched capacitors except fixed capacitors. Temporary overload of specific components shall also be considered. The harmonic filter requirements have to be fulfilled over the whole reactive power range for harmonic emission from the grid as well as SVC system.
| Training as per Annexure-E | Lot
| O&M supervision as per Annexure-F | Lot
Total Column 5 to be carried forward to Grand Summary.
Name Of Bidder :
Signature of Bidder :

## Schedule 3A
EnMasse
SCHEDULE No. 3A: Design Services
.+150/-50 MVAR Static VAR Compensator (SVC) at 132kV Gawadar Old Grid Station
Item | Description | Qty. | Unit Price |  | Total Price
|  |  | Local Currency Portion | Foreign Currency Portion | Local Currency Portion | Foreign Currency Portion
1 | 2 | 3 | 4 | 5 | 6=3x4 | 7=3x5
1 | The design of +150/-50 MVAR SVC capable of highspeed response to control system transient voltage stability, which shall meet the operational and system dynamic requirements, specified in specification and harmonic/power quality survey results attached herewith, using any configuration of Thyristor Controlled Reactors (TCR), Thyristor Switched Capacitors (TSC), fixed capacitors and harmonic filter circuits. The full dynamic range shall consist of thyristor controlled reactors and/or thyristor switched capacitors except fixed capacitors. Temporary overload of specific components shall also be considered. The harmonic filter requirements have to be fulfilled over the whole reactive power range for harmonic emission from the grid as well as SVC system, complete in all aspects along with all allied facilities as per international practice, ready to use, | Lot
2 | Design of associated civil works to house and install the plant supplied as per schedule 1 or 2 above Including civil works as per schedule No.4 | Lot
Total Column 6 and 7 to be carried forward to Grand Summary.
Name Of Bidder :
Signature of Bidder :

## Schedule 3B
EnMasse
SCHEDULE No. 3B: Design Services
.+150/-50 MVAR Static VAR Compensator (SVC) at 132kV Panjgoor Grid Station
Item | Description | Qty. | Unit Price |  | Total Price
|  |  | Local Currency Portion | Foreign Currency Portion | Local Currency Portion | Foreign Currency Portion
1 | 2 | 3 | 4 | 5 | 6=3x4 | 7=3x5
1 | The design of +150/-50MVAR SVC capable of highspeed response to control system transient voltage stability, which shall meet the operational and system dynamic requirements, specified in specification and harmonic/power quality survey results attached herewith, using any configuration of Thyristor Controlled Reactors (TCR), Thyristor Switched Capacitors (TSC), fixed capacitors and harmonic filter circuits. The full dynamic range shall consist of thyristor controlled reactors and/or thyristor switched capacitors except fixed capacitors. Temporary overload of specific components shall also be considered. The harmonic filter requirements have to be fulfilled over the whole reactive power range for harmonic emission from the grid as well as SVC system, complete in all aspects along with all allied facilities as per international practice, ready to use, | Lot
| Design of associated civil works to house and install the plant supplied as per schedule 1 or 2 above Including civil works as per schedule No.4 | Lot
Total Column 6 and 7 to be carried forward to Grand Summary.
Name Of Bidder :
Signature of Bidder :

## Schedule 4A
EnMasse
SCHEDULE No. 4A: Installation and Other Services (including civil works)
.+150/-50 MVAR Static VAR Compensator (SVC) at 132kV Gawadar Old Grid Station
Item | Description | Qty. | Unit Price |  | Total Price
|  |  | Local Currency Portion | Foreign Currency Portion | Local Currency Portion | Foreign Currency Portion
1 | 2 | 3 | 4 | 5 | 6=3x4 | 7=3x5
1 | Installation, testing and commissioning of the plant to be supplied against schedule No. 1 or 2. | Lot
2 | Construction (as per NTDC spec.) of associated civil works including control house building, office building transformers foundations, gantries foundations, transformer way, switch yard fence with gate, trenches, draw pit, approach road (within premises of the Plant), water supply and sewerage system including septic tank and collecting tank, etc., Complete in all aspects along with all allied facilities as per international practice, ready to use, and install the plant supplied as per schedule 1 or 2. Please refer to Supplementary Information, Section-6 for detail scope. | Lot
3 | Inland transportation and other incidental charges | Lot
The Contractar/Bidder is required to design the civil works according to the requirements (Building Code) of the relevant seismic zone issued by Government of Pakistan. In this context the Contractor/Bidder may obtain the relevant information from Earthquake Rehabilitation and Reconstruction Authority-ERRA (www.erra.gov.pk)
Total Column 6 and 7 to be carried forward to Grand Summary.
Name Of Bidder :
Signature of Bidder :

## Schedule 4B
EnMasse
SCHEDULE No. 4B: Installation and Other Services (including civil works)
.+150/-50 MVAR Static VAR Compensator (SVC) at 132kV Panjgoor Grid Station
Item | Description | Qty. | Unit Price |  | Total Price
|  |  | Local Currency Portion | Foreign Currency Portion | Local Currency Portion | Foreign Currency Portion
1 | 2 | 3 | 4 | 5 | 6=3x4 | 7=3x5
1 | Installation, testing and commissioning of the plant to be supplied against schedule No. 1 or 2. | Lot
2 | Construction (as per NTDC spec.) of associated civil works including control house building, office building transformers foundations, gantries foundations, transformer way, switch yard fence with gate, trenches, draw pit, approach road (within premises of the Plant), water supply and sewerage system including septic tank and collecting tank, etc., Complete in all aspects along with all allied facilities as per international practice, ready to use, and install the plant supplied as per schedule 1 or 2. Please refer to Supplementary Information, Section-6 for detail scope. | Lot
3 | Inland transportation and other incidental charges | Lot
The Contractar/Bidder is required to design the civil works according to the requirements (Building Code) of the relevant seismic zone issued by Government of Pakistan. In this context the Contractor/Bidder may obtain the relevant information from Earthquake Rehabilitation and Reconstruction Authority-ERRA (www.erra.gov.pk)
Total Column 6 and 7 to be carried forward to Grand Summary.
Name Of Bidder :
Signature of Bidder :

## Schedule 5
EnMasse
SCHEDULE No. 5 Grand Summary
.+150/-50 MVAR Static VAR Compensator (SVC) at 132kV Gawadar Old and 132kV Panjgoor Grid Station
Item | Description | Total
|  | Foreign | Local Million Pak. Rupees
1 | Schedule 1(A to B): Plant and Mandatory Spare Parts Supplied from Abroad
2 | Schedule 2(A to B): Plant and Mandatory Spare Parts Supplied from Within the Employer's Country
3 | Schedule 3(A to B): Design Services
4 | Schedule 4(A to B): Installation and Other Services including Civil Works Including Inland Transportation
5 | Provisional Sum
Grand Total to be carried forward to Letter of Bid
Name Of Bidder :
Signature of Bidder :

## Spares GWD
EnMasse
Mandatory Spare Parts
.+150/-50 MVAR Static VAR Compensator (SVC) at 132kV Gawadar Old Grid Station
Item | Description | Qty | Unit Price |  | Total Price
|  |  | EXW Local Parts Local Currency | CIP Imported Parts Foreign Currency | Local Currency Portion | Foreign Currency Portion
1 | 2 | 3 | 4 | 5 | 6 = 3 x 4 | 7 = 3 x 5
1 | Control System
1 | Central processor unit | 1
2 | Digital I/O card | 1
3 | Digital I/O card | 1
4 | Digital I/O card for trigger set | 1
5 | Profibus communication card | 1
6 | LAN card | 1
7 | FLASH Memory Card | 3
8 | I/O module | 1
9 | I/O module | 1
10 | Control cable | 1
11 | Control cable | 1
12 | Logic module | 1
13 | Voltage to voltage transformer | 1
14 | Current to voltage transformer | 1
15 | Varistor | 1
16 | RS232/TTY converter | 1
17 | POWER OPTOCOUPLER | 1
18 | INPUT OPTICAL COUPLER DEK-OE | 1
19 | PLC TERMINAL PLC-RSC-24DC/21 Relay module | 1
20 | OPTOCOUPLER EMG10-OV, 110VDC, 1A | 1
21 | VARIOFACE MODULE FLK-D37 SUB/B Special terminal block | 1
22 | UNIVERSAL ISOLATING AMPLIFIER | 1
23 | CONTACTOR RELAY, 3NO+1NC, Auxiliary Relay | 1
24 | 6MD High Voltage Interface Unit I/O unit | 1
25 | Time synchronization system | 1
26 | LAN switch | 1
27 | Plug for Profibus connection | 1
28 | Control unit power supply | 1
29 | RS232-RS485 converter | 1
30 | Fan | 1
31 | LAN switch | 1
2 | Protection System
1 | Transformer differential protection | 1
2 | Numerical overcurrent protection relay | 1
3 | Numerical overcurrent protection relay | 1
4 | Capacitor protection relay | 1
5 | Lock out Relay | 1
6 | Trip supervision relay | 1
7 | DIODE-MODUL | 1
8 | Voltage supervision relay | 1
9 | Auxiliary relay 2NO+2NC, DC 24V | 1
10 | Auxiliary relay 2NO+2NC, DC 110V | 1
11 | Auxiliary switch block | 1
12 | Relay module | 1
13 | FAULT ANNUNCIATOR | 1
14 | FT 1 Testswitch | 1
3 | HMI System
1 | Rack PC | 1
4 | Digital Fault Recorder
1 | DDAU Module (DC Data Acquisition Unit) type Input module for DC values | 1
2 | VDAU Module (Voltage Data Acquisition Unit) type Input module for voltages | 1
3 | CDAU Module (Current Data Acquisition Unit) type Input module for currents | 1
4 | Ethernet communication card | 1
5 | Central processor unit | 1
6 | Synchronizing unit | 1
5 | Power Supply C&P
1 | Net filter SIFI C 10 A, 250 V | 1
2 | Net filter SIFI C 1 A, 250 V | 1
3 | Net filter SIFI C 6 A, 250 V | 1
4 | CIRC.BR. CURRENT SENS. T55 4.5KA 1-P C1 MCB | 1
5 | CIRC.BR. CURRENT SENS. T55 4.5KA 1-P C6 MCB | 1
6 | CIRC.BR. CURRENT SENS. T55 4.5KA 1-P C10 MCB | 1
7 | CIRC.BR. CURRENT SENS. T55 4.5KA 2-P C1 MCB | 1
8 | CIRC.BR. CURRENT SENS. T55 4.5KA 2-P C0 MCB | 1
9 | CIRC.BR. CURRENT SENS. T55 4.5KA 2-P C6 MCB | 1
10 | CIRC.BR. CURRENT SENS. T55 4.5KA 2-P C4 MCB | 1
11 | CIRC.BR. CURRENT SENS. T55 4.5KA 2-P C10 MCB | 1
12 | CIRC.BR. CURRENT SENS. T55 4.5KA 2-P C16 MCB | 1
13 | AUXILIARY SWITCH 1S+1OE F.5SX | 1
14 | Powertronic C354-H-L-R DC/DC chopper | 1
15 | Powertronic C354-H-L-R-WM DC/DC chopper | 1
16 | Powertronic C554-H-L-R DC/DC chopper | 1
17 | Powertronic C658-H-L-R-U DC/DC chopper | 1
18 | Powertronic C659-H-L-R-U (48V) DC/DC chopper | 1
19 | 1 set of terminals | 1
6 | Thyristor Valve & Valve Base Electronic
Items and quantities per each thyristor branch
1 | Thyristor, 5 inch type | 3
2 | Snubber capacitor | 2
3 | DC grading resistor | 4
4 | Snubber resistor | 4
5 | Optical fiber, connecting multi mode star coupler and thyristor | 5
6 | Thyristor voltage monitoring board | 2
7 | Set of spare parts for valve cooling system | 1
8 | Fiber optic adapter for firing check fiber optics (2pcs) | 1
9 | Fiber optic plug connector for firing check fiber optics | 2
Valve base electronics rack:
10 | Microcontroller printed circuit board | 1
11 | Light emitter printed circuit board | 1
12 | Light receiver printed circuit board | 1
13 | Adapter module printed circuit board | 1
7 | Capacitors
1 | STF1 Capacitor | 3
2 | STF2 Capacitor | 3
3 | Surge capacitor | 1
4 | Set of rack insulators | 1
8 | Reactors
1 | TCR Reactor (half coil) | 0
2 | STF Reactor | 0
3 | STF Resistor | 1
4 | Set of spare insulators | 1
9 | Power Transformer
1 | HV-Bushing | 1
2 | LV Bushing | 1
3 | Oil and winding temp. Indicator | 1
4 | Winding temperature indicator | 1
5 | Gas relay | 1
6 | Gasket set | 1
10 | Surge Arrester
1 | HV Surge arrester | 1
2 | LV Surge arrestor | 1
11 | MV - Switch Gear Unit
1 | Spare part package | 1
12 | Thyristor Cooling Plant
1 | Pump fine water circuit | 1
3 | Level Switch (expansion tank) | 1
4 | Ion Exchanger | 1
5 | Ion Exchanger resin filling | 1
6 | Conductance meter | 1
7 | Solenoid valve | 1
8 | Filter cartridges | 1
9 | Digital thermometer | 1
10 | Digital pressure gauge | 1
11 | Flow meter fine water circuit | 1
12 | Set control spares | 1
13 | Miscellaneous
1 | Set AC/DC Supply spares | 1

## Spares PNJGR
EnMasse
Mandatory Spare Parts
.+150/-50 MVAR Static VAR Compensator (SVC) at 132kV Panjgoor Grid Station
Item | Description | Qty | Unit Price |  | Total Price
|  |  | EXW Local Parts Local Currency | CIP Imported Parts Foreign Currency | Local Currency Portion | Foreign Currency Portion
1 | 2 | 3 | 4 | 5 | 6 = 3 x 4 | 7 = 3 x 5
1 | Control System
1 | Central processor unit | 1
2 | Digital I/O card | 1
3 | Digital I/O card | 1
4 | Digital I/O card for trigger set | 1
5 | Profibus communication card | 1
6 | LAN card | 1
7 | FLASH Memory Card | 3
8 | I/O module | 1
9 | I/O module | 1
10 | Control cable | 1
11 | Control cable | 1
12 | Logic module | 1
13 | Voltage to voltage transformer | 1
14 | Current to voltage transformer | 1
15 | Varistor | 1
16 | RS232/TTY converter | 1
17 | POWER OPTOCOUPLER | 1
18 | INPUT OPTICAL COUPLER DEK-OE | 1
19 | PLC TERMINAL PLC-RSC-24DC/21 Relay module | 1
20 | OPTOCOUPLER EMG10-OV, 110VDC, 1A | 1
21 | VARIOFACE MODULE FLK-D37 SUB/B Special terminal block | 1
22 | UNIVERSAL ISOLATING AMPLIFIER | 1
23 | CONTACTOR RELAY, 3NO+1NC, Auxiliary Relay | 1
24 | 6MD High Voltage Interface Unit I/O unit | 1
25 | Time synchronization system | 1
26 | LAN switch | 1
27 | Plug for Profibus connection | 1
28 | Control unit power supply | 1
29 | RS232-RS485 converter | 1
30 | Fan | 1
31 | LAN switch | 1
2 | Protection System
1 | Transformer differential protection | 1
2 | Numerical overcurrent protection relay | 1
3 | Numerical overcurrent protection relay | 1
4 | Capacitor protection relay | 1
5 | Lock out Relay | 1
6 | Trip supervision relay | 1
7 | DIODE-MODUL | 1
8 | Voltage supervision relay | 1
9 | Auxiliary relay 2NO+2NC, DC 24V | 1
10 | Auxiliary relay 2NO+2NC, DC 110V | 1
11 | Auxiliary switch block | 1
12 | Relay module | 1
13 | FAULT ANNUNCIATOR | 1
14 | FT 1 Testswitch | 1
3 | HMI System
1 | Rack PC | 1
4 | Digital Fault Recorder
1 | DDAU Module (DC Data Acquisition Unit) type Input module for DC values | 1
2 | VDAU Module (Voltage Data Acquisition Unit) type Input module for voltages | 1
3 | CDAU Module (Current Data Acquisition Unit) type Input module for currents | 1
4 | Ethernet communication card | 1
5 | Central processor unit | 1
6 | Synchronizing unit | 1
5 | Power Supply C&P
1 | Net filter SIFI C 10 A, 250 V | 1
2 | Net filter SIFI C 1 A, 250 V | 1
3 | Net filter SIFI C 6 A, 250 V | 1
4 | CIRC.BR. CURRENT SENS. T55 4.5KA 1-P C1 MCB | 1
5 | CIRC.BR. CURRENT SENS. T55 4.5KA 1-P C6 MCB | 1
6 | CIRC.BR. CURRENT SENS. T55 4.5KA 1-P C10 MCB | 1
7 | CIRC.BR. CURRENT SENS. T55 4.5KA 2-P C1 MCB | 1
8 | CIRC.BR. CURRENT SENS. T55 4.5KA 2-P C0 MCB | 1
9 | CIRC.BR. CURRENT SENS. T55 4.5KA 2-P C6 MCB | 1
10 | CIRC.BR. CURRENT SENS. T55 4.5KA 2-P C4 MCB | 1
11 | CIRC.BR. CURRENT SENS. T55 4.5KA 2-P C10 MCB | 1
12 | CIRC.BR. CURRENT SENS. T55 4.5KA 2-P C16 MCB | 1
13 | AUXILIARY SWITCH 1S+1OE F.5SX | 1
14 | Powertronic C354-H-L-R DC/DC chopper | 1
15 | Powertronic C354-H-L-R-WM DC/DC chopper | 1
16 | Powertronic C554-H-L-R DC/DC chopper | 1
17 | Powertronic C658-H-L-R-U DC/DC chopper | 1
18 | Powertronic C659-H-L-R-U (48V) DC/DC chopper | 1
19 | 1 set of terminals | 1
6 | Thyristor Valve & Valve Base Electronic
Items and quantities per each thyristor branch
1 | Thyristor, 5 inch type | 3
2 | Snubber capacitor | 2
3 | DC grading resistor | 4
4 | Snubber resistor | 4
5 | Optical fiber, connecting multi mode star coupler and thyristor | 5
6 | Thyristor voltage monitoring board | 2
7 | Set of spare parts for valve cooling system | 1
8 | Fiber optic adapter for firing check fiber optics (2pcs) | 1
9 | Fiber optic plug connector for firing check fiber optics | 2
Valve base electronics rack:
10 | Microcontroller printed circuit board | 1
11 | Light emitter printed circuit board | 1
12 | Light receiver printed circuit board | 1
13 | Adapter module printed circuit board | 1
7 | Capacitors
1 | STF1 Capacitor | 3
2 | STF2 Capacitor | 3
3 | Surge capacitor | 1
4 | Set of rack insulators | 1
8 | Reactors
1 | TCR Reactor (half coil) | 0
2 | STF Reactor | 0
3 | STF Resistor | 1
4 | Set of spare insulators | 1
9 | Power Transformer
1 | HV-Bushing | 1
2 | LV Bushing | 1
3 | Oil and winding temp. Indicator | 1
4 | Winding temperature indicator | 1
5 | Gas relay | 1
6 | Gasket set | 1
10 | Surge Arrester
1 | HV Surge arrester | 1
2 | LV Surge arrestor | 1
11 | MV - Switch Gear Unit
1 | Spare part package | 1
12 | Thyristor Cooling Plant
1 | Pump fine water circuit | 1
3 | Level Switch (expansion tank) | 1
4 | Ion Exchanger | 1
5 | Ion Exchanger resin filling | 1
6 | Conductance meter | 1
7 | Solenoid valve | 1
8 | Filter cartridges | 1
9 | Digital thermometer | 1
10 | Digital pressure gauge | 1
11 | Flow meter fine water circuit | 1
12 | Set control spares | 1
13 | Miscellaneous
1 | Set AC/DC Supply spares | 1